## 管线增压储气电厂不连续运行10 小时平衡
说明：全部管道连为一体储气，民用气时间按每天3小时计。电厂上午、下午各运行3.5小时，晚上运行3小时。 | [39 empty] | 储器温度oC
电厂管道及储罐容积：
| 储罐数 | 罐容积m3 |  |  | 总容积 m3 | 储气温度oC | 最低压力MPa(a) |  | 存底气量104Nm3
| 0.05 | 2000 |  |  | 100 | 30 | 0.5 |  | 0.047694 | [30 empty] | 30
管线长度 | 管径mm | 壁厚mm | 长度km |  | 管道容积m3 | [17 empty] | 民用气 |  | 公福用气 |  | 工业用气
龙~阀组 | 559 | 7.1 | 12 |  | 2797.3381 | 20 | 0.6 |  | 1.6556
阀组-烟 | 457 | 6.4 | 83 |  | 12862.4801 | 20 | 0.6 |  | 7.6127 | [13 empty] | 日用气量 | 小时平均 | 日用气量 | 小时平均 | 日用气量 | 小时平均
黄-招支线 | 219 | 5.6 | 21 |  | 712.1966 | 20 | 0.6 |  | 0.42151 | [12 empty] | 烟台市 | 9.4943 | 3.1648 | 3.8012 | 0.21118 | 10.6496 | 0.44373 | [12 empty] | 20
蓬莱支线 | 219 | 5.6 | 21 |  | 712.1966 | 20 | 0.6 |  | 0.42151 | [12 empty] | 蓬莱市 | 1.1519 | 0.38396 | 0.56198 | 0.031221 | 0.22688 | 0.0094535
阀组-莱线 | 273 | 6.4 | 72 |  | 3828.57 | 20 | 0.6 |  | 2.2659 | [12 empty] | 龙口市 | 2.1676 | 0.72254 | 2.1676 | 0.12042 |  | 0
[5 empty] | 18115.4433 | 20 | 0.6 |  | 10.7217 | [12 empty] | 招远市 | 1.0821 | 0.36069 | 0.30717 | 0.017065 | 0.10702 | 0.0044592
[22 empty] | 莱州市 | 2.5411 | 0.84704 | 0.38745 | 0.021525 | 0.25411 | 0.010588
[6 empty] | 求解1 | 求解2 | [14 empty] | 合计 | 16.4369 | 5.479 | 7.2254 | 0.40141 | 11.2376 | 0.46824
[6 empty] | 0 | 0
| 处理厂来气量 |  | 4.3 | 104Nm3/h |  | 2 | 1 | [5 empty] | 各城市民用天然气随时间变化，管道系统提供部分储气调峰能力。 | [8 empty] | 日用气总量 | 34.9054 | x104Nm3/d
| 去电厂储罐 |  | 0.0093248 |  |  | 1 | 1
| 储罐出气 |  | 0.01084 |  |  | 1 | 1
| 电厂用气 |  | 6.83 |  |  | 100 | 100
|  | 处理厂 |  | 电厂储罐 | [8 empty] | 储气管道系统 | [10 empty] | 烟台市 |  |  | 蓬莱市 |  |  | 龙口市 |  |  | 招远市 |  |  | 莱州市
| 时间 | 来气 | 进气 | 出气 | 储气量 |  | 去电厂 | 进入管线 | 电厂用气 | 管线储气量 | 管线压力 | 烟台市 | 蓬莱市 | 龙口市 | 龙口区 | 黄城区 | 招远市 | 莱州市 | 总用气量 | 管线储气量 | 管线压力 |  |  |  | 民用 | 公福 | 工业 | 民用 | 公福 | 工业 | 民用 | 公福 | 工业 | 民用 | 公福 | 工业 | 民用 | 公福 | 工业
|  | 104Nm3/h | 104Nm3/h | 104Nm3/h | x104m3 | 压力 MPa(a) | 104Nm3/h | 104Nm3/h | 104Nm3/h | 104Nm3/h | MPa(a) | 104Nm3/h | 104Nm3/h | 104Nm3/h | 104Nm3/h | 104Nm3/h | 104Nm3/h | 104Nm3/h | 104Nm3/h | 104Nm3/h | MPa(a) |  |  | 时间 | 104Nm3/h | 104Nm3/h | 104Nm3/h | 104Nm3/h | 104Nm3/h | 104Nm3/h | 104Nm3/h | 104Nm3/h | 104Nm3/h | 104Nm3/h | 104Nm3/h | 104Nm3/h | 104Nm3/h | 104Nm3/h | 104Nm3/h
| 23:00 | 4.3 | 0.0093248 |  | 0.033825 | 0.34042 |  | 4.2907 |  | 11.7455 | 0.6573 | 0.65491 | 0.040674 | 0.12042 | 0.024085 | 0.096339 | 0.021524 | 0.032113 | 0.89373 | 14.1186 | 0.75849 |  |  | 23:00 |  | 0.21118 | 0.44373 |  | 0.031221 | 0.0094535 |  | 0.12042 | 0 |  | 0.017065 | 0.0044592 |  | 0.021525 | 0.010588
| 0:00 | 4.3 | 0.0093248 |  | 0.04315 | 0.43427 |  | 4.2907 |  | 16.0362 | 0.89741 | 0.44373 | 0.0094535 | 0 | 0 | 0 | 0.0044592 | 0.010588 | 0.46824 | 17.941 | 0.96385 |  |  | 0:00 |  |  | 0.44373 |  |  | 0.0094535 |  |  | 0 |  |  | 0.0044592 |  |  | 0.010588
| 1:00 | 4.3 | 0.0093248 |  | 0.052475 | 0.52811 |  | 4.2907 |  | 20.3269 | 1.1375 | 0.44373 | 0.0094535 | 0 | 0 | 0 | 0.0044592 | 0.010588 | 0.46824 | 21.7635 | 1.1692 |  |  | 1:00 |  |  | 0.44373 |  |  | 0.0094535 |  |  | 0 |  |  | 0.0044592 |  |  | 0.010588
| 2:00 | 4.3 | 0.0093248 |  | 0.061799 | 0.62196 |  | 4.2907 |  | 24.6176 | 1.3776 | 0.44373 | 0.0094535 | 0 | 0 | 0 | 0.0044592 | 0.010588 | 0.46824 | 25.5859 | 1.3746 |  |  | 2:00 |  |  | 0.44373 |  |  | 0.0094535 |  |  | 0 |  |  | 0.0044592 |  |  | 0.010588
| 3:00 | 4.3 | 0.0093248 |  | 0.071124 | 0.7158 |  | 4.2907 |  | 28.9082 | 1.6177 | 0.44373 | 0.0094535 | 0 | 0 | 0 | 0.0044592 | 0.010588 | 0.46824 | 29.4084 | 1.5799 |  |  | 3:00 |  |  | 0.44373 |  |  | 0.0094535 |  |  | 0 |  |  | 0.0044592 |  |  | 0.010588
| 4:00 | 4.3 | 0.0093248 |  | 0.080449 | 0.80965 |  | 4.2907 |  | 33.1989 | 1.8579 | 0.44373 | 0.0094535 | 0 | 0 | 0 | 0.0044592 | 0.010588 | 0.46824 | 33.2308 | 1.7853 |  |  | 4:00 |  |  | 0.44373 |  |  | 0.0094535 |  |  | 0 |  |  | 0.0044592 |  |  | 0.010588
| 5:00 | 4.3 | 0.0093248 |  | 0.089774 | 0.9035 |  | 4.2907 |  | 37.4896 | 2.098 | 0.44373 | 0.0094535 | 0 | 0 | 0 | 0.0044592 | 0.010588 | 0.46824 | 37.0532 | 1.9906 |  |  | 5:00 |  |  | 0.44373 |  |  | 0.0094535 |  |  | 0 |  |  | 0.0044592 |  |  | 0.010588
| 6:00 | 4.3 | 0.0093248 |  | 0.099099 | 0.99734 |  | 4.2907 |  | 41.7803 | 2.3381 | 3.8197 | 0.42463 | 0.84296 | 0.16859 | 0.67437 | 0.38221 | 0.87915 | 6.5172 | 34.8267 | 1.871 |  |  | 6:00 | 3.1648 | 0.21118 | 0.44373 | 0.38396 | 0.031221 | 0.0094535 | 0.72254 | 0.12042 | 0 | 0.36069 | 0.017065 | 0.0044592 | 0.84704 | 0.021525 | 0.010588
| 7:00 | 4.3 | 0.0093248 |  | 0.10842 | 1.0912 |  | 4.2907 |  | 46.0709 | 2.5782 | 0.65491 | 0.040674 | 0.12042 | 0.024085 | 0.096339 | 0.021524 | 0.032113 | 0.89373 | 38.2236 | 2.0535 |  |  | 7:00 |  | 0.21118 | 0.44373 |  | 0.031221 | 0.0094535 |  | 0.12042 | 0 |  | 0.017065 | 0.0044592 |  | 0.021525 | 0.010588
| 8:00 | 4.3 | 0.0093248 |  | 0.10842 | 1.0912 |  | 4.2907 |  | 50.3616 | 2.8183 | 0.65491 | 0.040674 | 0.12042 | 0.024085 | 0.096339 | 0.021524 | 0.032113 | 0.89373 | 41.6206 | 2.236 |  |  | 8:00 |  | 0.21118 | 0.44373 |  | 0.031221 | 0.0094535 |  | 0.12042 | 0 |  | 0.017065 | 0.0044592 |  | 0.021525 | 0.010588
| 9:00 | 4.3 |  | 0.01084 | 0.097584 | 0.9821 | 4.3 | 0 | 2.5192 | 47.8424 | 2.6773 | 0.65491 | 0.040674 | 0.12042 | 0.024085 | 0.096339 | 0.021524 | 0.032113 | 0.89373 | 38.2077 | 2.0526 |  |  | 9:00 |  | 0.21118 | 0.44373 |  | 0.031221 | 0.0094535 |  | 0.12042 | 0 |  | 0.017065 | 0.0044592 |  | 0.021525 | 0.010588
| 10:00 | 4.3 |  | 0.01084 | 0.086744 | 0.87301 | 4.3 | 0 | 2.5192 | 45.3233 | 2.5364 | 0.65491 | 0.040674 | 0.12042 | 0.024085 | 0.096339 | 0.021524 | 0.032113 | 0.89373 | 34.7948 | 1.8693 |  |  | 10:00 |  | 0.21118 | 0.44373 |  | 0.031221 | 0.0094535 |  | 0.12042 | 0 |  | 0.017065 | 0.0044592 |  | 0.021525 | 0.010588
| 11:00 | 4.3 |  | 0.01084 | 0.075905 | 0.76392 | 4.3 | 0 | 2.5192 | 42.8041 | 2.3954 | 3.8197 | 0.42463 | 0.84296 | 0.16859 | 0.67437 | 0.38221 | 0.87915 | 6.5172 | 25.7584 | 1.3838 |  |  | 11:00 | 3.1648 | 0.21118 | 0.44373 | 0.38396 | 0.031221 | 0.0094535 | 0.72254 | 0.12042 | 0 | 0.36069 | 0.017065 | 0.0044592 | 0.84704 | 0.021525 | 0.010588
| 12:00 | 4.3 |  | 0.0054198 | 0.070485 | 0.70937 | 2.15 | 2.15 | 1.2596 | 43.6945 | 2.4452 | 0.65491 | 0.040674 | 0.12042 | 0.024085 | 0.096339 | 0.021524 | 0.032113 | 0.89373 | 25.7551 | 1.3836 |  |  | 12:00 |  | 0.21118 | 0.44373 |  | 0.031221 | 0.0094535 |  | 0.12042 | 0 |  | 0.017065 | 0.0044592 |  | 0.021525 | 0.010588
| 13:00 | 4.3 | 0.0093248 |  | 0.070485 | 0.70937 |  | 4.2907 |  | 47.9852 | 2.6853 | 0.65491 | 0.040674 | 0.12042 | 0.024085 | 0.096339 | 0.021524 | 0.032113 | 0.89373 | 29.1521 | 1.5661 |  |  | 13:00 |  | 0.21118 | 0.44373 |  | 0.031221 | 0.0094535 |  | 0.12042 | 0 |  | 0.017065 | 0.0044592 |  | 0.021525 | 0.010588
| 14:00 | 4.3 | 0.0093248 |  | 0.070485 | 0.70937 |  | 4.2907 |  | 52.2759 | 2.9254 | 0.65491 | 0.040674 | 0.12042 | 0.024085 | 0.096339 | 0.021524 | 0.032113 | 0.89373 | 32.549 | 1.7486 |  |  | 14:00 |  | 0.21118 | 0.44373 |  | 0.031221 | 0.0094535 |  | 0.12042 | 0 |  | 0.017065 | 0.0044592 |  | 0.021525 | 0.010588
| 15:00 | 4.3 |  | 0.01084 | 0.059645 | 0.60028 | 4.3 | 0 | 2.5192 | 49.7567 | 2.7845 | 0.65491 | 0.040674 | 0.12042 | 0.024085 | 0.096339 | 0.021524 | 0.032113 | 0.89373 | 29.1361 | 1.5653 |  |  | 15:00 |  | 0.21118 | 0.44373 |  | 0.031221 | 0.0094535 |  | 0.12042 | 0 |  | 0.017065 | 0.0044592 |  | 0.021525 | 0.010588
| 16:00 | 4.3 |  | 0.01084 | 0.048806 | 0.49119 | 4.3 | 0 | 2.5192 | 47.2376 | 2.6435 | 0.65491 | 0.040674 | 0.12042 | 0.024085 | 0.096339 | 0.021524 | 0.032113 | 0.89373 | 25.7232 | 1.3819 |  |  | 16:00 |  | 0.21118 | 0.44373 |  | 0.031221 | 0.0094535 |  | 0.12042 | 0 |  | 0.017065 | 0.0044592 |  | 0.021525 | 0.010588
| 17:00 | 4.3 |  | 0.01084 | 0.037966 | 0.3821 | 4.3 | 0 | 2.5192 | 44.7184 | 2.5025 | 0.65491 | 0.040674 | 0.12042 | 0.024085 | 0.096339 | 0.021524 | 0.032113 | 0.89373 | 22.3103 | 1.1986 |  |  | 17:00 |  | 0.21118 | 0.44373 |  | 0.031221 | 0.0094535 |  | 0.12042 | 0 |  | 0.017065 | 0.0044592 |  | 0.021525 | 0.010588
| 18:00 | 4.3 |  | 0.0054198 | 0.032546 | 0.32755 | 2.15 | 2.15 | 1.2596 | 45.6088 | 2.5523 | 3.8197 | 0.42463 | 0.84296 | 0.16859 | 0.67437 | 0.38221 | 0.87915 | 6.5172 | 16.6835 | 0.89629 |  |  | 18:00 | 3.1648 | 0.21118 | 0.44373 | 0.38396 | 0.031221 | 0.0094535 | 0.72254 | 0.12042 | 0 | 0.36069 | 0.017065 | 0.0044592 | 0.84704 | 0.021525 | 0.010588
| 19:00 | 4.3 | 0.0093248 |  | 0.057019 | 0.57385 |  | 4.2907 |  | 15.0123 | 0.84011 | 0.65491 | 0.040674 | 0.12042 | 0.024085 | 0.096339 | 0.021524 | 0.032113 | 0.89373 | 20.0805 | 1.0788 |  |  | 19:00 |  | 0.21118 | 0.44373 |  | 0.031221 | 0.0094535 |  | 0.12042 | 0 |  | 0.017065 | 0.0044592 |  | 0.021525 | 0.010588
| 20:00 | 4.3 |  | 0.01084 | 0.046179 | 0.46476 | 4.3 | 0 | 2.5192 | 12.4932 | 0.69914 | 0.65491 | 0.040674 | 0.12042 | 0.024085 | 0.096339 | 0.021524 | 0.032113 | 0.89373 | 16.6676 | 0.89543 |  |  | 20:00 |  | 0.21118 | 0.44373 |  | 0.031221 | 0.0094535 |  | 0.12042 | 0 |  | 0.017065 | 0.0044592 |  | 0.021525 | 0.010588
| 21:00 | 4.3 |  | 0.01084 | 0.03534 | 0.35566 | 4.3 | 0 | 2.5192 | 9.974 | 0.55816 | 0.65491 | 0.040674 | 0.12042 | 0.024085 | 0.096339 | 0.021524 | 0.032113 | 0.89373 | 13.2547 | 0.71208 |  |  | 21:00 |  | 0.21118 | 0.44373 |  | 0.031221 | 0.0094535 |  | 0.12042 | 0 |  | 0.017065 | 0.0044592 |  | 0.021525 | 0.010588
| 22:00 | 4.3 |  | 0.01084 | 0.0245 | 0.24657 | 4.3 | 0 | 2.5192 | 7.4549 | 0.41718 | 0.65491 | 0.040674 | 0.12042 | 0.024085 | 0.096339 | 0.021524 | 0.032113 | 0.89373 | 9.8418 | 0.52873 |  |  | 22:00 |  | 0.21118 | 0.44373 |  | 0.031221 | 0.0094535 |  | 0.12042 | 0 |  | 0.017065 | 0.0044592 |  | 0.021525 | 0.010588
| 合计气量 | 103.2 | 0.1119 | 0.1084 |  |  | 43 | 55.7881 | 25.1916 |  |  | 23.9451 | 1.9407 | 4.3352 |  |  | 1.4963 | 3.1827 | 35.767
| 黄色表示电厂开机发电的时间 | [5 empty] | 电厂开机时，气体处理厂外输干气全部输送到电厂， | [7 empty] | 日用气量平衡＝ |  | -0.86705 | x104Nm3/d
[7 empty] | 不足部分从管道系统中抽气补充。合计供电厂6.83万方天然气 | [12 empty] | 储气管道系统压力随时间变化曲线，这是采用静态
模型计算的结果，仅是平均压力，未能反应各接点
的压力变化。
输气管线示意图：
f559x6.4 L=12km
蓬莱市
f219.1x6.4 L=5km
输气首站
f323.9x7.1 L=2.5km
[13 empty] | 黄城区 |  |  |  | f559x6.4 L=21km
|  |  |  | 发电厂 |  | 龙口区
f219.1x6.4 L=2km
f457x6.4 L=16km
阀组
[5 empty] | f273x6.4 L=13km |  |  | f273x6.4 L=14km | [5 empty] | f457x6.4 L=12km |  |  |  | f457x6.4 L=57km
烟台市
辛庄
|  |  |  | f114.3x4 L=2km |  |  |  | f219x6.4 L=21km
[6 empty] | f273x6.4 L=41km |  | 招远市
莱州市
输气首站流程图
运行时间表：
|  | 时间： | F1 | F2 | F3 | F4 | F5 | 1#压缩机 | 2＃压缩机
|  | 23:00 | closed | open | closed | closed | closed | stoped | stoped |  |  | 中海公司来气直接进入输气管道系统储存
…
|  | ~3:00 | open | closed | closed | open | closed | run | stoped |  |  | 由于管道系统的压力达到1.6MPa，与中海公司来气压力平衡，开始起动1＃压缩机向管道增压储气。
…
|  | 8:01 | open | closed | open | closed | open | run | run |  |  | 电厂开始发电
…
|  | 11:30 | open | closed | closed | open | closed | run | stoped |  |  | 电厂停机
…
|  | 14:01 | open | closed | open | closed | open | run | run |  |  | 电厂开始发电
…
|  | 17:30 | open | closed | closed | open | closed | run | stoped |  |  | 电厂停机
…
|  | 19:01 | open | closed | open | closed | open | run | run |  |  | 电厂开始发电
…
|  | 21:59 | closed | open | closed | closed | closed | stoped | stoped |  |  | 电厂停机 | 中海公司来气直接进入输气管道系统储存
|  | 22:01 | closed | open | closed | closed | closed | stoped | stoped |  |  | 电厂停机 | 中海公司来气直接进入输气管道系统储存
Note on B4: xcs: 电厂不设储罐，0.05表示去电厂的管道储气容积
Note on F12: xcs: 所有管道系统合计总容积
Note on G14: 孙晓春: 限定储罐最高压力1.6MPa(a)计算最大进罐气量
Note on H14: 孙晓春: 限定储罐最终压力0.5MPa(a)计算最大出气量
Note on J12: xcs: 储气管道达到最低压力是，管道内部的存气量，不能被利用。
1＃
压缩机
2＃
压缩机
发电厂
至外输管网
中海公司来气
F1
F2
F3
F4
F5